## Input-data
Solar hot water production
Project | yyy | 2021-05-26
Simulation ENERGY
Energy comsumption per year | xxxx | kWh/Year | [5 empty] | Site preparation | 5000 | €HT
[8 empty] | ETF unit installation | 3800 | €HT/unité
Number of ETF units | 4 | [6 empty] | Prix estimé | 20200 | €HT
Solar irradiance value (Calsol INES) | LE MANS | Albedo | 0.8
Unit (kWh / m² / day) | Jan. | Feb | Mar. | Apl. | May | Juin | Luly | Aug | Sep | Oct. | Nov. | Dec. | Year
Direct irradiance | 0.66 | 2.17 | 2.18 | 2.95 | 3.81 | 2.57 | 2.98 | 3.86 | 2.69 | 1.73 | 1.22 | 1.02 | 2.32
Diffus irradiance | 0.55 | 1.44 | 1.67 | 2.29 | 2.59 | 2.52 | 2.66 | 2.46 | 2.06 | 1.5 | 1.04 | 0.8 | 1.7983
Cold water temperature (°C) | 7.5 | 7.8 | 9.4 | 11 | 12 | 14 | 15 | 15 | 14 | 11 | 9.3 | 7.8 | 11.15
Water requirement L/day | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942
Numbre of operation day | 15 | 28 | 31 | 30 | 31 | 30 | 15 | 31 | 30 | 31 | 30 | 31
Hot water tempareture °C | 80
Heat loss from boiler system | 37%
Simulation FINANCEMENT and ROIC
Investment eligible to public aid | 20200 | euros | Aid | 0%
Investment non eligible to public aid | 0 | euros
Capital loan | 20200 | euros
Loan rate | 1.2%
Period | 10 | Year
Energy price increasing /year | 1% | 3% | 5%
Energy cost | 0.17 | euro HT/ kWh |  |  |  |  | 30
²

## Results-Tech
Solar energy simulation results |  | Project | yyy
|  | Date | 2021-05-26
Total conventional energy need | 39856.6146 | kWh/year | Propane | 3113.798 | kg/year
Energy saving | 20744.2744 | kWh/year | Propane saving | 1620.6464 | kg/year
Solar energy rate | 52.05%
Reduction of CO2 emissions | 4771.1831 | kg/year

## Calcul-Tech (hidden)
Prévision Energétique (Le Mans) |  |  | (valeurs d'irradiation issus de Calsol de l'INES)
conso. de gaz par an |  |  | xxxx | kWh/Year | #REF! | #REF! | #REF! | #REF! |  | #REF! |  | #REF! | #REF!
Tube / ballon |  |  | 30
Nombre de ballon |  |  | 4 |  | Rendement des tubes |  | 50% |  | Coefficient angle (direct) |  | 0.7691
Nombre de Tubes |  |  | 120 |  | Réseaux et échangeurs |  | 80% |  | Coefficient réfléchis+diffus |  | 1.3 | (réfléchie = 0,3 diffus)
Unité (kWh/m² x jours) |  |  | Janvier | Février | Mars | Avril | Mai | Juin | Juillet | Août | Septembre | Octobre | Novembre | Décembre | Année
Irradiation Globale (45°) |  |  | 1.21 | 3.61 | 3.85 | 5.24 | 6.4 | 5.09 | 5.64 | 6.32 | 4.75 | 3.23 | 2.26 | 1.82 | 4.1183
Irradiation Direct |  |  | 0.66 | 2.17 | 2.18 | 2.95 | 3.81 | 2.57 | 2.98 | 3.86 | 2.69 | 1.73 | 1.22 | 1.02 | 2.32
Irradiation Diffus |  |  | 0.55 | 1.44 | 1.67 | 2.29 | 2.59 | 2.52 | 2.66 | 2.46 | 2.06 | 1.5 | 1.04 | 0.8 | 1.7983
température eau froide °C |  |  | 7.5 | 7.8 | 9.4 | 11 | 12 | 14 | 15 | 15 | 14 | 11 | 9.3 | 7.8
Irradiation Direct |  | (kWh / mois) | 118.7761 | 728.9736 | 810.7972 | 1061.7868 | 1417.0355 | 925.0143 | 536.2923 | 1435.6317 | 968.2056 | 643.4308 | 439.1118 | 379.3638 | 9464.4195
Irradiation Diffus+Reflé |  | (kWh / mois) | 334.6097 | 1635.3289 | 2099.7266 | 2786.3863 | 3256.4622 | 3066.2417 | 1618.2942 | 3093.0104 | 2506.5309 | 1885.982 | 1265.4331 | 1005.857 | 24553.8629
Irradiation Globale |  | (kWh / mois) | 453.3859 | 2364.3025 | 2910.5238 | 3848.1731 | 4673.4977 | 3991.2559 | 2154.5865 | 4528.6421 | 3474.7365 | 2529.4128 | 1704.5449 | 1385.2209 | 34018.2824
Potentiel solaire |  | (kWh / mois) | 181.3543 | 945.721 | 1164.2095 | 1539.2692 | 1869.3991 | 1596.5024 | 861.8346 | 1811.4569 | 1389.8946 | 1011.7651 | 681.818 | 554.0883 | 13607.313
Potentiel solaire |  | (kWh / jour) | 5.8501 | 33.7757 | 37.5551 | 51.309 | 60.3032 | 53.2167 | 27.8011 | 58.4341 | 46.3298 | 32.6376 | 22.7273 | 17.8738
Conso d'eau litre/jour |  |  | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942 | 942
Besoins en énergie |  | (kWh / jour) | 79.4128 | 79.0842 | 77.3316 | 75.5791 | 74.4837 | 72.293 | 71.1977 | 71.1977 | 72.293 | 75.5791 | 77.4412 | 79.0842
nb de jour opérationel |  |  | 15 | 28 | 31 | 30 | 31 | 30 | 15 | 31 | 30 | 31 | 30 | 31 | 333
ECS par mois (L) |  |  | 14130 | 26376 | 29202 | 28260 | 29202 | 28260 | 14130 | 29202 | 28260 | 29202 | 28260 | 29202 | 313686
Besoins en énergie total | E0 | (kWh / mois) | 1191.1919 | 2214.3572 | 2397.2805 | 2267.3721 | 2308.9953 | 2168.7907 | 1067.9651 | 2207.1279 | 2168.7907 | 2342.9512 | 2323.2349 | 2451.6098 | 25109.6672
Perte de chauffe et de maintien |  |  | 699.5889 | 1300.4955 | 1407.9266 | 1331.6312 | 1356.0766 | 1273.7342 | 627.2176 | 1296.2497 | 1273.7342 | 1376.0189 | 1364.4395 | 1439.8343 | 14746.9474
Energie de chauffe (s/Sth)/mois | E0' | (kWh / mois) | 1890.7807 | 3514.8527 | 3805.2071 | 3599.0033 | 3665.072 | 3442.5249 | 1695.1827 | 3503.3776 | 3442.5249 | 3718.9701 | 3687.6744 | 3891.4441 | 39856.6146
Energie de chauffe (s/Sth)/jour | E0' | (kWh / jour) | 60.9929 | 125.5305 | 122.7486 | 119.9668 | 118.2281 | 114.7508 | 54.6833 | 113.0122 | 114.7508 | 119.9668 | 122.9225 | 125.5305
Besoins de Chauffage /jour |  | (kWh / jour) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Besoins de Chauffage/mois |  | (kWh / mois) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energie de chauffe (s/Sth)/mois | E0' | (kWh / mois) | 1890.7807 | 3514.8527 | 3805.2071 | 3599.0033 | 3665.072 | 3442.5249 | 1695.1827 | 3503.3776 | 3442.5249 | 3718.9701 | 3687.6744 | 3891.4441 | 39856.6146
Energie de chauffe (a/Sth)/mois | E0' | (kWh / mois) | 1540.9863 | 2864.605 | 3101.2438 | 2933.1877 | 2987.0337 | 2805.6578 | 1381.5739 | 2855.2528 | 2805.6578 | 3030.9606 | 3005.4547 | 3171.5269 | 32483.1409
Energie de chauffe (a/Sth)/jour | E0' | (kWh / jour) | 102.7324 | 102.3073 | 100.0401 | 97.7729 | 96.3559 | 93.5219 | 92.1049 | 92.1049 | 93.5219 | 97.7729 | 100.1818 | 102.3073
|  |  | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE
Solaire Thermique utile | E1 | (kWh / mois) | 87.7521 | 945.721 | 1164.2095 | 1539.2692 | 1869.3991 | 1596.5024 | 417.0167 | 1811.4569 | 1389.8946 | 1011.7651 | 681.818 | 554.0883 | 13068.8928
Energie appoint (gaz ou autre) | E2' | (kWh / mois) | 1511.7125 | 1738.0316 | 1689.3072 | 997.5009 | 602.2469 | 784.035 | 891.7993 | 542.0693 | 1067.0877 | 1823.7249 | 2248.7412 | 2599.6043 | 16495.8609
Taux de couverture par mois | E1/E0 |  | 7.367% | 42.71% | 48.56% | 67.89% | 80.96% | 73.61% | 39.05% | 82.07% | 64.09% | 43.18% | 29.35% | 22.6% | 52.05%
température eau chaude °C |  |  | Janvier: 80
Perte de chauffe et de maintien |  |  | Janvier: 37%; Février: #REF!
Réduction de temps de chauffe |  |  | Janvier: 50%

## Results-auto-Financement
Results of financement simulation
| Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1 | Costs without STE | 6775.6245 | 6978.8932 | 7188.26 | 7403.9078 | 7626.0251 | 7854.8058 | 8090.45 | 8333.1635 | 8583.1584 | 8840.6531 | 9105.8727 | 9379.0489 | 9660.4204 | 9950.233 | 10248.74 | 10556.2022 | 10872.8882 | 11199.0749 | 11535.0471 | 11881.0985
2 | Loan repayment | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Gas remaining to buy | 3249.0978 | 3346.5708 | 3446.9679 | 3550.3769 | 3656.8882 | 3766.5949 | 3879.5927 | 3995.9805 | 4115.8599 | 4239.3357 | 4366.5158 | 4497.5113 | 4632.4366 | 4771.4097 | 4914.552 | 5061.9886 | 5213.8482 | 5370.2637 | 5531.3716 | 5697.3127
4 | System maintenance | 0 | 0 | 0 | 0 | 0 | 200 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 302.5179
5 | Costs with STE | 5393.7299 | 5491.2028 | 5591.5999 | 5695.009 | 5801.5203 | 6111.2269 | 6230.2248 | 6352.7926 | 6479.0374 | 6609.0695 | 4598.3706 | 4736.3217 | 4878.4114 | 5024.7637 | 5175.5066 | 5330.7718 | 5490.695 | 5655.4159 | 5825.0783 | 5999.8307
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Enegy saving (1-5) €HT/Y | 1381.8946 | 1487.6904 | 1596.6601 | 1708.8988 | 1824.5048 | 1743.5789 | 1860.2252 | 1980.3709 | 2104.121 | 2231.5836 | 4507.5021 | 4642.7272 | 4782.009 | 4925.4692 | 5073.2333 | 5225.4303 | 5382.1932 | 5543.659 | 5709.9688 | 5881.2679
7 | Energy saving €HT/m | 115.1579 | 123.9742 | 133.055 | 142.4082 | 152.0421 | 145.2982 | 155.0188 | 165.0309 | 175.3434 | 185.9653 | 375.6252 | 386.8939 | 398.5007 | 410.4558 | 422.7694 | 435.4525 | 448.5161 | 461.9716 | 475.8307 | 490.1057
[13 empty] | Financing simulation results (self-financing) |  |  |  |  | avec | 3%
[13 empty] | Project: | yyy |  | Date: | 2021-05-26
[12 empty] | Total Invest | 20200 | euros |  |  |  | Saving € / Year
[12 empty] | Grant | 0 | euros |  |  |  | 1ère année | 1381.8946 | euros
[12 empty] | Capital loan | 20200 | euros |  |  |  | 6 ème année | 1824.5048 | euros
[12 empty] | Loan period | 10 | Year |  |  |  | 11 ème année | 4507.5021 | euros
[12 empty] | Loan rate | 1.2% |  |  |  |  | 20 èmé années | 5881.2679 | euros

## Calcul -financement (hidden)
Investissement financement
|  | Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Total Invest | 20200
N° | [22 empty] | Grant | 0
1 | Costs without STE | 3% | 6775.6245 | 6978.8932 | 7188.26 | 7403.9078 | 7626.0251 | 7854.8058 | 8090.45 | 8333.1635 | 8583.1584 | 8840.6531 | 9105.8727 | 9379.0489 | 9660.4204 | 9950.233 | 10248.74 | 10556.2022 | 10872.8882 | 11199.0749 | 11535.0471 | 11881.0985 | Capital loan | 20200
[23 empty] | Period | 10
2 | Loan repayment |  | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 2144.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Loan rate | 1.2%
3 | Gas remaining to buy | 47.95% | 3249.0978 | 3346.5708 | 3446.9679 | 3550.3769 | 3656.8882 | 3766.5949 | 3879.5927 | 3995.9805 | 4115.8599 | 4239.3357 | 4366.5158 | 4497.5113 | 4632.4366 | 4771.4097 | 4914.552 | 5061.9886 | 5213.8482 | 5370.2637 | 5531.3716 | 5697.3127
4 | System maintenance | [6 empty] | 200 | 206 | 212.18 | 218.5454 | 225.1018 | 231.8548 | 238.8105 | 245.9748 | 253.354 | 260.9546 | 268.7833 | 276.8468 | 285.1522 | 293.7067 | 302.5179
5 | Costs with STE |  | 5393.7299 | 5491.2028 | 5591.5999 | 5695.009 | 5801.5203 | 6111.2269 | 6230.2248 | 6352.7926 | 6479.0374 | 6609.0695 | 4598.3706 | 4736.3217 | 4878.4114 | 5024.7637 | 5175.5066 | 5330.7718 | 5490.695 | 5655.4159 | 5825.0783 | 5999.8307
6 | Enegy saving (1-5) €HT/y |  | 1381.8946 | 1487.6904 | 1596.6601 | 1708.8988 | 1824.5048 | 1743.5789 | 1860.2252 | 1980.3709 | 2104.121 | 2231.5836 | 4507.5021 | 4642.7272 | 4782.009 | 4925.4692 | 5073.2333 | 5225.4303 | 5382.1932 | 5543.659 | 5709.9688 | 5881.2679
7 | Energy saving €HT/m |  | 115.1579 | 123.9742 | 133.055 | 142.4082 | 152.0421 | 145.2982 | 155.0188 | 165.0309 | 175.3434 | 185.9653 | 375.6252 | 386.8939 | 398.5007 | 410.4558 | 422.7694 | 435.4525 | 448.5161 | 461.9716 | 475.8307 | 490.1057
| Energy consumption before STE |  | 1: 39856.6146; 2: kWh/year
| Energy cost |  | 1: 0.17; 2: € HT/kWh
| Energy saving |  | 1: 20744.2744; 2: kWh/year
| Economie d'énergie |  | 1: 52.05%
| Hypothese energy cost raising |  | 1: 3%; 2: / Year

## Results-ROIC
Simulation resultas ROI and ROIC
|  |  |  | Project : | yyy |  | Date : | 2021-05-26
[6 empty] | Return of invertement (ROI) | 5.728 | ans
[6 empty] | Return of invested capitals (ROIC) | 17.46%
[6 empty] | Energy saving rate | 52.05%
[6 empty] | Invested capitals (except aid) | 20200 | euros
[6 empty] | Public aid | 0 | euros | 0%
[6 empty] | Total investement (with aid) | 20200 | euros
[6 empty] | Energy cost | 0.17 | euro HT/ kWh
Energy price increasing /year | 1% | 3% | 5%

## Summary_Tech-Design
Tubes / ETF unit | 30
ETF units | 4 |  |  | SYSTÈME FENGTECH SIMULATION | Projet | yyy
Numbre of tubes | 120 |  |  |  | Date | 2021-05-26
Designation | Calcul
Hot water requirement | 313686 | Liter/Y
Conventional energy need without STE | 39856.6146 | kWh/Y |  | Propane | 3113.798 | kg/year
Total uesful energy need | 25109.6672 | kWh/Y | E0 | Propane | 1961.6928 | kg/year
Useful Solar thermal energy | 13068.8928 | kWh/Y | E1 | Propane | 1021.0073 | kg/year
Conventional energy consumption with solar thermal energy | 16495.8609 | kWh/Y |  | Propane | 1288.7391 | kg/year
Capture surface in front of a unit | 4 | m² |  | Useful solar energy per m² of front capture surface | 816.8058 | kWh/m²/year
Effcetive capture area in front of a unit | 3 | m² |  | Useful solar energy per m² of front effective capture area | 1089.0744 | kWh/m²/year
Solar energy rate | 52.05% |  | Ve | Energy saving per m² of front capture surface | 1296.5171 | kWh/m²/year
Energy saving | 20744.2744 | kWh/Y | Va | Propane saving | 1620.6464 | kg/year
Reduction of CO2 emissions | 4771.1831 | kg/Y |  | Investment/(Energy saving per year) | 0.97376 | €/kWh

## calcul-ROIC (hidden)
|  |  |  | Taux 1 |  | Taux 2 |  | Taux 3 |  |  | Taux 1 | Taux 2 | Taux 3 | Taux 1 | Taux 2 | Taux 3
|  |  |  | Economie par an | Economie cumulée | Economie par an | Economie cumulée | Economie par an | Economie cumulée | Année | ROI 1 | ROI 2 | ROI 3 | Taux de rendement
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20200 | -20200 | -20200 | 0% | 0% | 0%
|  |  |  | 3526.5266 | 3526.5266 | 3526.5266 | 3526.5266 | 3526.5266 | 3526.5266 | 1 | -16673.4734 | -16673.4734 | -16673.4734 | 17.46% | 17.46% | 17.46%
|  |  |  | 3561.7919 | 7088.3185 | 3632.3224 | 7158.8491 | 3702.853 | 7229.3796 | 2 | -13111.6815 | -13041.1509 | -12970.6204 | 17.63% | 17.98% | 18.33%
|  |  |  | 3597.4098 | 10685.7284 | 3741.2921 | 10900.1412 | 3887.9956 | 11117.3752 | 3 | -9514.2716 | -9299.8588 | -9082.6248 | 17.81% | 18.52% | 19.25%
|  |  |  | 3633.3839 | 14319.1123 | 3853.5309 | 14753.6721 | 4082.3954 | 15199.7706 | 4 | -5880.8877 | -5446.3279 | -5000.2294 | 17.99% | 19.08% | 20.21%
Total Investment | 20200 |  |  | 3669.7178 | 17988.8301 | 3969.1368 | 18722.8089 | 4286.5152 | 19486.2858 | 5 | -2211.1699 | -1477.1911 | -713.7142 | 18.17% | 19.65% | 21.22%
Investment eligible to public aid | 20200 |  |  | 3706.4149 | 21695.245 | 4088.2109 | 22811.0198 | 4500.8409 | 23987.1267 | 6 | 1495.245 | 2611.0198 | 3787.1267 | 18.35% | 20.24% | 22.28%
Investment non eligible to public aid | 0 |  |  | 3743.4791 | 25438.7241 | 4210.8572 | 27021.877 | 4725.883 | 28713.0097 | 7 | 5238.7241 | 6821.877 | 8513.0097 | 18.53% | 20.85% | 23.4%
|  |  |  | 3780.9139 | 29219.638 | 4337.183 | 31359.06 | 4962.1771 | 33675.1869 | 8 | 9019.638 | 11159.06 | 13475.1869 | 18.72% | 21.47% | 24.57%
Public aid | 0% |  |  | 3818.723 | 33038.361 | 4467.2984 | 35826.3584 | 5210.286 | 38885.4728 | 9 | 12838.361 | 15626.3584 | 18685.4728 | 18.9% | 22.12% | 25.79%
Energy price increasing /year | 1% | 3% | 5% | 3856.9103 | 36895.2713 | 4601.3174 | 40427.6758 | 5470.8003 | 44356.2731 | 10 | 16695.2713 | 20227.6758 | 24156.2731 | 19.09% | 22.78% | 27.08%
|  |  |  | 3895.4794 | 40790.7506 | 4739.3569 | 45167.0327 | 5744.3403 | 50100.6134 | 11 | 20590.7506 | 24967.0327 | 29900.6134 | 19.28% | 23.46% | 28.44%
Savings in the first year | 3526.5266 | 20744.2744 | 0.17 | 3934.4341 | 44725.1848 | 4881.5376 | 50048.5703 | 6031.5573 | 56132.1707 | 12 | 24525.1848 | 29848.5703 | 35932.1707 | 19.48% | 24.17% | 29.86%
Current energy bill | 6775.6245 | 39856.6146 |  | 3973.7785 | 48698.9632 | 5027.9838 | 55076.5541 | 6333.1352 | 62465.3059 | 13 | 28498.9632 | 34876.5541 | 42265.3059 | 19.67% | 24.89% | 31.35%
Energy saving | 52.05% |  |  | 4013.5163 | 52712.4795 | 5178.8233 | 60255.3774 | 6649.7919 | 69115.0979 | 14 | 32512.4795 | 40055.3774 | 48915.0979 | 19.87% | 25.64% | 32.92%
|  |  |  | 4053.6514 | 56766.131 | 5334.188 | 65589.5653 | 6982.2815 | 76097.3794 | 15 | 36566.131 | 45389.5653 | 55897.3794 | 20.07% | 26.41% | 34.57%
Average ROIC (at 15 years) | 18.73% | 21.65% | 25.11% | 4094.188 | 60860.3189 | 5494.2136 | 71083.7789 | 7331.3956 | 83428.775 | 16 | 40660.3189 | 50883.7789 | 63228.775 | 20.27% | 27.2% | 36.29%
Average ROIC (at 20 years) | 19.22% | 23.46% | 28.86% | 4135.1298 | 64995.4487 | 5659.04 | 76742.8189 | 7697.9654 | 91126.7404 | 17 | 44795.4487 | 56542.8189 | 70926.7404 | 20.47% | 28.02% | 38.11%
|  |  |  | 4176.4811 | 69171.9299 | 5828.8112 | 82571.6302 | 8082.8637 | 99209.604 | 18 | 48971.9299 | 62371.6302 | 79009.604 | 20.68% | 28.86% | 40.01%
|  |  |  | 4218.2459 | 73390.1758 | 6003.6755 | 88575.3057 | 8487.0068 | 107696.6109 | 19 | 53190.1758 | 68375.3057 | 87496.6109 | 20.88% | 29.72% | 42.01%
|  |  |  | 4260.4284 | 77650.6042 | 6183.7858 | 94759.0915 | 8911.3572 | 116607.9681 | 20 | 57450.6042 | 74559.0915 | 96407.9681 | 21.09% | 30.61% | 44.12%
|  | Payback (years) = | 5.728
|  | ROIC (at first year) = | 17.46%